|  | EUROPEAN COMMISSION |
| --- | --- |

CONSTRUCT 08/830

Draft

COMMISSION DECISION ../…/EC

xx/xx/2008

implementing Council Directive 89/106/EEC as regards the classification of the resistance to fire performance of construction products, construction works and parts thereof and amending Commission Decision 2000/367/EC

(Text with EEA relevance)

EN

Draft

COMMISSION DECISION …/…/EC

xx/xx/2008

implementing Council Directive 89/106/EEC as regards the classification of the resistance to fire performance of construction products, construction works and parts thereof and amending Commission Decision 2000/367/EC

(Text with EEA relevance)

THE COMMISSION OF THE EUROPEAN COMMUNITIES,

Having regard to the Treaty establishing the European Community,

Having regard to Council Directive 89/106 of 21 December 1988, on the approximation of laws, regulations and administrative provisions of the Member States relating to construction products, as amended by Council Directive 93/68/EEC, and in particular Articles 3, 6 and 20 thereof,

Having regard to Commission Decision 2000/367/EC of 3 May 2000 implementing the Council Directive 89/106/EEC as regards the classification of the resistance to fire performance of construction products, construction works and parts thereof,

Whereas:

- Articles 3(2) and 3(3) of Directive 89/106/EEC state that in order to take account of different levels of protection for the construction works that may prevail at national, regional or local levels, each essential requirement may give rise to the establishment of classes in the interpretative documents; whereas these documents have been published as the “Communication of the Commission with regard to the interpretative documents of Directive 89/106/EEC”.

- Paragraph 4.2.1 of interpretative document No 2 justifies the need for different levels of the Essential Requirement as function of the type, use and location of the construction work, its layout and the availability of the emergency facilities.

- Paragraph 2.2 of the interpretative document No 2 lists a number of interrelated measures for the satisfaction of the Essential Requirement "Safety in case of fire" that together contribute to define the fire safety strategy that can be developed in different ways in Member States.

- Paragraph 4.3.1.3 of the interpretative document No 2 identifies one of these measures prevailing in Member States that relates to the resistance to fire performance of construction products and/ or parts of construction works.

- To enable the resistance to fire performance of construction products and construction works or parts thereof to be evaluated, the harmonised solution consists in a system of classes that is included in interpretative document No.2.

- This system of classes has been adapted to technical progress in a mandate from the Commission to the European standardisation bodies, CEN and CENELEC.

- Article 6(3) of Directive 89/106/EEC states that the Member States may determine the performance levels to be observed in their territory only within the classifications adopted at Community level and only subject to the use of all or some classes or one class.

- Certain families of construction products are not covered in Decision 2000/367/EC, and therefore the Decision 2000/367/EC needs to be amended in order to include these product families.

- The measures provided for in the present decision are in accordance with the opinion of the Standing Committee on Construction.

HAS ADOPTED THIS DECISION:

Article 1

The annex to the Commission Decision 2000/367/EC is amended as described in the annex of this decision.

Article 2

This Decision is addressed to the Member States.

Done at Brussels,

For the Commission

ANNEX

The following tables are added after table 6:

"7. Products to be used in smoke and heat management systems

| Applies to: | Smoke control ducts and smoke control dampers |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Classification: | Refer to EN13501-4 for definitions and classification procedure. |  |  |  |  |  |  |  |  |  |
| E300 |  |  | 30 |  | 60 | 90 | 120 |  |  |  |
| E600 |  |  | 30 |  | 60 | 90 | 120 |  |  |  |
| EI |  |  | 30 |  | 60 | 90 | 120 |  |  |  |
| Notes | The classification is completed by the suffix ‘single’ or ‘multi’ to indicate respectively the suitability for single or multi-compartment use only. In addition, the symbols ‘ve’ and/or ‘ho’ indicate the suitability of ducts for vertical and/or horizontal use, whilst ‘ved’, ‘vew’, ‘vedw’ and/or ‘hod’, ‘how’, ‘hodw’ indicate the suitability for dampers for vertical and/or horizontal use together with mounting in a duct or in a wall or both respectively. A classification may be completed by ‘(i → o)’, ‘(o → i)’, or ‘(i ↔ o)’ to indicate whether the element has been tested and fulfils the requirements from the inside or outside only or both. The addition of the symbol ‘S’ indicates the satisfaction of higher restrictions on leakage rates than the minimum normally applied for the classification. The numbers ‘500’, ‘1000’, ‘1500’ indicate the suitability for use up to these values of pressure (Pascals), measured at ambient. For dampers with an E600 classification, the addition of ‘HOT 400/30’ indicates that the damper has the ability to be opened or closed during a period of 30 minutes under temperature conditions below 400oC. Symbols ‘AA’ or ‘MA’ indicates automatic or manual activation or intervention. Also for dampers, ‘C300’, C10000’, Cmod’ indicates the suitability for use in smoke control only systems only, combined smoke control and environmental systems, or in combined smoke control and environmental systems respectively. |  |  |  |  |  |  |  |  |  |

| Applies to: | Smoke barriers |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Classification: | Refer to EN13501-4 for definitions and classification procedure. |  |  |  |  |  |  |  |  |  |
| D600 |  |  | 30 |  | 60 | 90 | 120 |  |  | A |
| DH |  |  | 30 |  | 60 | 90 | 120 |  |  | A |
| Notes | A can be any time over 120 minutes. |  |  |  |  |  |  |  |  |  |

8. Products to be used in smoke and heat exhaust ventilation systems

| Applies to: | Natural and powered smoke and heat exhaust ventilators and their connecting joints |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Classification: | Refer to EN13501-4 for definitions and classification procedure. |  |  |  |  |  |  |  |  |  |
| Fn |  |  | 30 |  | 60 | 90 | 120 |  |  |  |
| Bn |  |  | 30 |  |  |  |  |  |  |  |
| Notes | The F classification relates only to powered smoke and heat exhaust ventilators (fans) and connecting joints. The B classification relates only to natural smoke and heat ventilators. The n suffix denotes the exposure condition (temperature). |  |  |  |  |  |  |  |  |  |

OJ L 40, 11.2.1989, p 12

OJ L 220, 30.8.1993, p 1

OJ L 133, 6.6.2000, p 26

OJ C 62, 28.2.1994, p 1